FIREROLL VR60 INSULATED FIRE SHUTTERS

SPECIFICATION 3-7

Fire Resistance

Tested to EN 1634-1 for integrity and insulation of 60 minutes (EI60 rating in accordance with EN 13501-2).

Curtain

Constructed from 63 x 36mm synthetic material laths infilled with high-performance insulation.

Bottom Rail

Comprising a standard lath fitted with an extruded PVC bottom seal.

## Guides

The side guides are formed from galvanised steel channels with a black intumescent insert and prepared for fixing to the opening structure.

## End Brackets

Fabricated from galvanised steel of adequate thickness relative to door size and supplied with steel plates for fixing to the structure.

## Roller

The roller is manufactured from mild steel tube of sufficient diameter and wall thickness to resist deflection and is mounted in bearings on each end plate.

Finish

The shutter curtain is supplied in a grey self-finish as standard.

## Weight

Approximately 50 kgs per m².

Operation

Electrical operation is by means of a direct drive three-phase motor mounted on one endplate.  In the event of fire and / or mains failure, a 24volt DC auxiliary drive unit closes the door.

Controls

A control panel is supplied for mounting at high level which incorporates batteries and a facility for an incoming fire signal.  Cables between panel and motor are to be flameproof. Low level control is by wall-mounted push buttons.

To specify state:

FIREROLL VR60 Insulated Fire Shutters shall be by

Bolton Gate Company, Waterloo Street, Bolton BL1 2SP, UK Tel: 01204 871001

E-mail: sales@boltongate.co.uk Web: www.boltongate.co.uk.

Issue Date: April 2018