SMOKEBARRIER D120 CURTAINS

SPECIFICATION 18-2

Performance

The curtains have been tested and meet the requirements of EN 12101-1(D120).

Curtain

Constructed from specially coated grey fibre-glass material tested to withstand temperatures of up to 600˚C.

Bottom Rail

The lower edge of the curtain incorporates a triangular steel section to act as a weight bar.

## Endplates

Fabricated from galvanised mild of adequate thickness relative to curtain size onto which the tube is fixed.

## Casing

The casing is manufactured from galvanised steel and is 158 x 150mm for single curtains and 252 x 150mm for multiple curtains.

Finish

Galvanised as standard.  The casings and bottom rails are also available in a polyester powder coated finish in a range of standard RAL colours at extra cost.

## Weight

Approximately 20 kgs per linear metre of width.

Operation

Electrical operation is by means of a 240-volt AC tubular motor mounted inside the barrel.  A control panel is provided at high level and operates up to ten curtains.  Closure in a fire condition is via gravity with a controlled descent.  A single-phase socket is required within one metre of the control panel position.

Fire Activation

In a fire condition, activation is initiated by an incoming signal from the fire alarm system.

To specify state:

Smokebarrier D120 Curtains shall be by

Bolton Gate Company, Waterloo Street, Bolton BL1 2SP, UK Tel: 01204 871001

E-mail: sales@boltongate.co.uk Web: www.boltongate.co.uk

Issue Date: January 2018