FIREROLL ACOUSTIC ROLLER SHUTTERS

SPECIFICATION 3-11

Fire Resistance

Tested to EN1634-1 and achieved a rating of EW120 (integrity and radiation reduction) in accordance with EN 13501-2.

Acoustic Rating

When independently tested, the door achieved a weighted sound reduction index Rw of 25 dB (32dB if a double roller design is used).

Curtain

Constructed from 100mm flat section galvanised steel laths with acoustic / fire resisting infill and steel endlocks fitted to alternate laths to prevent lateral movement. The bottom rail is a lath fitted with a galvanised steel trim section.

## Guides

The side guides are formed from galvanised steel channels and are prepared for fixing to the opening structure by means of continuous fixing angles.

## Endplates

Fabricated from mild steel of adequate thickness relative to door size and supplied with angles for fixing to the structure.

## Roller

The roller is manufactured from mild steel tube of sufficient diameter and wall thickness to resist deflection and is mounted in bearings on each end plate. A galvanised steel casing is supplied as standard.

Finish

Galvanised as standard.  A factory finish is available which comprises a white plastisol internal face (coil side) with the external face polyester powder coated to a standard RAL colour.

## Weight

Approximately 50 kgs per m².

Operation

Electrical operation is by means of a single or three-phase Speedsafe motor mounted on one endplate.  The standard unit is pre-wired obviating the need for a site electrician. Standard controls are by means of open / close / stop push buttons fitted adjacent to the shutter.

Fire Activation

In a fire condition, closure is activated by a fusible link or an auto re-set solenoid.  Descent is always at a controlled speed.

To specify state:

Fireroll Acoustic Roller Shutters shall be by

Bolton Gate Company, Waterloo Street, Bolton BL1 2SP, UK Tel: 01204 871001

E-mail: sales@boltongate.co.uk Web: www.boltongate.co.uk

Issue Date: April 2018